## Slide 1
REJECTION ANALYSIS
& ACTION PLAN
Water Cooler Supply - GeM Contract GEMC-511687763924679
Northern Railway | Moradabad Division
Supplier: M/s Cool Home (India), Greater Noida
Date: July 2026

## Slide 2
TENDER & CONTRACT OVERVIEW
GeM Bid No.
GEM/2026/B/7299831
Contract No.
GEMC-511687763924679
Contract Date
15-04-2026
Buyer
Northern Railway, Moradabad
Supplier
M/s Cool Home (India)
Item
Water Cooler, Storage Type, 150 L/hr
Quantity
29 Units
Rate/Unit
Rs. 35,200
Total Value
Rs. 10,20,800
Inspection
RITES (Pre-Dispatch)
Consignee
SSE/ACSP/MB, Moradabad
REJECTION ALERT
Rejection Advice No: 76673-26-00257 Date: 22-07-2026 Qty Invoiced: 29 Nos. Qty Received: 29 Nos. Qty Rejected: 29 Nos. (ALL) Reason: "Product supplied is not as per specifications (Under rated and poor Quality)"
Confidential - For Internal Use Only

## Slide 3
COMPRESSOR ANALYSIS - THE ROOT CAUSE
CRITICAL FINDING: GODREJ GE153H IS A 200W REFRIGERATOR COMPRESSOR
Used in a Water Cooler that requires 1550W - This is 7.75x under-powered for the application
Source: IndiaMART (Jupiter Refrigeration, Ahmedabad) - Verified Product Listing
Parameter
Tender Required
GE153H Actual
Gap
Power Rating
1550 Watt
200 Watt
7.75x UNDER
Cooling Capacity
150 L/hr
Not rated for water cooler
NOT APPLICABLE
Application
Water Cooler (IS 1475)
Refrigerator / Deep Freeze
WRONG APPLICATION
Compressor Type
Per IS 1475
Reciprocating (Fridge)
MISMATCH
Voltage
230V AC, 50Hz
220-240V AC, 50Hz
OK
Refrigerant
R134A
R134A
OK
Confidential - For Internal Use Only

## Slide 4
ROOT CAUSE ANALYSIS
PRIMARY ISSUE: Under-Rated Compressor (CONFIRMED)
GE153H = 200W refrigerator compressor
Tender requires 1550W for 150 L/hr cooling
Compressor is 7.75x under-powered
Designed for fridges, NOT water coolers
Cannot deliver 150 L/hr cooling capacity
SECONDARY ISSUE: Poor Quality
Construction quality below expected standards
Outer body material: SS 202 (tender may require SS 304)
Tender requires IS 1475 compliance
Possible issues with PUF insulation, finishing
Overall build quality did not meet Railway standards
CRITICAL OBSERVATION: RITES Inspection Gap
RITES was mandated for Pre-Dispatch Inspection at seller premises - RITES cleared the goods
Despite RITES clearance, ALL 29 units rejected at consignee site
Rejection remarks: "Consignee (RITES) may take necessary action against Inspecting Officials"
This indicates negligence by RITES inspecting officials - they cleared a 200W fridge compressor for a 1550W water cooler
OPPORTUNITY: RITES clearance can be used as defense argument
Confidential - For Internal Use Only

## Slide 5
FULL TECHNICAL SPECIFICATION vs WHAT WAS SUPPLIED
Parameter
Tender Requirement
What Was Supplied
Status
Cooling Capacity
150 L/hr
GE153H - 200W fridge compressor
NON-CONFORMING
Max Power
1550 Watt
200 Watt (7.75x under)
NON-CONFORMING
Voltage
230V AC, 50Hz, Single Phase
220-240V AC, 50Hz
OK
Inner Tank Material
SS 304 Food Grade
SS 304 Food Grade
OK
Outer Body Material
SS (Check spec)
SS 202
CHECK NEEDED
Compressor
Per IS 1475
Godrej GE153H (200W fridge)
FAILED
ISI Mark / IS 1475
Required
Claimed
FAILED INSPECTION
Compressor Warranty
5 Years
To be verified
PENDING
Overall Warranty
1 Year Comprehensive
To be verified
PENDING
Confidential - For Internal Use Only

## Slide 6
DEFENSE STRATEGIES
OPTION 1: Challenge the Rejection
Argue RITES pre-dispatch clearance = specs were met
Demand specific test data from consignee
Question testing methodology & conditions
Check for transit damage possibilities
VERY HIGH RISK - compressor is clearly under-rated
OPTION 2: Accept & Replace (RECOMMENDED)
Accept rejection diplomatically
Remove 29 units before free period expires
Supply replacement units with correct compressor (1500W+)
Request 30-45 day timeline from buyer
BEST for preserving Railway relationship
OPTION 3: Modify In-Situ
Replace 200W compressor with 1500W+ rated model
Retest and resubmit to consignee
Keep cooler bodies if quality is acceptable
COSTLY and TIME-CONSUMING
Buyer agreement uncertain
RECOMMENDATION
Go with Option 2 - Accept & Replace
Negotiate with Sameer Mathur (SSE/ACSP/MB)
Ensure removal of stock immediately
Source correct 1500W+ compressor before resupply
Document everything for future compliance
Confidential - For Internal Use Only

## Slide 7
IMMEDIATE ACTION PLAN
URGENT
Remove 29 rejected units
Avoid ground rent liability
Today
URGENT
Compressor issue CONFIRMED
200W fridge compressor in 1550W cooler
DONE
HIGH
Source correct compressor (1500W+)
Must deliver 150 L/hr for water cooler
This Week
HIGH
Review RITES inspection cert
Build defense - RITES cleared wrong compressor
This Week
HIGH
Check IS 1475 specific requirements
Identify all non-conformances
Next 3 Days
MEDIUM
Draft replacement proposal to buyer
Formal communication with timeline
Next 7 Days
MEDIUM
Get quotes for correct compressor
Compare Godrej/Copeland/Emerson options
Next 7 Days
LOW
Review warranty claims
5-year compressor warranty may apply
Next 30 Days
Confidential - For Internal Use Only

## Slide 8
KEY CONTACTS & DOCUMENT REFERENCES
KEY CONTACTS
Consignee: Sameer Mathur, SSE/ACSP/MB
Phone: 0591-2412081
Email: sameer.mathur75@gov.in
Buyer: SrDMM MB (vivekk.joshii@gov.in)
Phone: 0591-2413141
Inspection Agency: RITES
RITES NR: nrinspn@rites.com
Phone: +9188000018691
Supplier Rep: Vipin Kumar (Cool Home India)
DOCUMENT REFERENCES
Tender: GEM/2026/B/7299831 (27-03-2026)
Contract: GEMC-511687763924679 (15-04-2026)
Rejection Advice: 76673-26-00257 (22-07-2026)
DRR No: 76673-26-00256
Challan: DC/2026-27/54 (20-07-2026)
Joint Note: 22-07-2026
Technical Spec: Model SWCFCRIO150150
Compressor: Godrej GE153H (200W - CONFIRMED)
IS Standard: IS 1475 (Part-1) 2001
Confidential - For Internal Use Only

## Slide 9
KEY TAKEAWAYS
01
GE153H = 200W fridge compressor used in 1550W water cooler (7.75x under-powered)
02
Rejection is TECHNICALLY JUSTIFIED - compressor cannot deliver 150 L/hr
03
RITES cleared wrong compressor at pre-dispatch - negligence angle available
04
IMMEDIATE: Remove 29 units to avoid ground rent liability
05
BEST PATH: Accept & replace with correctly rated 1500W+ compressor units
Prepared for Internal Review | July 2026